## Slide 1: Presentation for PFS ICS infrastructure design review
Atsushi Shimono (PFS Project Office)
2017/03/09 0800-1200 JST
draft
pages as filled draft are marked with left up corner marks, but 1st draft status

## Slide 2: Agenda
PFS ICS infrastructure design review
  Overview of targets in this review
  Brief overview of PFS ICS design
  Network
  Link over fiber on telescope
  Storage and image data handling
  VM infrastructure
  ICS infrastructure support hardware
  Database server and its replication/backup
  ICS infrastructure status monitoring and defect detection
  Procedure on instrument exchange
  Procedures for power failure detection and handling
  Hardware delivery to Subaru
Discussions on interfaces between Subaru and PFS
  Network connection to Subaru (data flow, V-LAN)
  Access control to/from PFS network
  System alert handling (items to STS)
  Engineering data archive (during on-site AIT, independent unit test)

## Slide 3: Overview of targets in this review
Network
Link over fiber on telescope
Storage and image data handling
VM infrastructure
ICS infrastructure support hardware
Database server and its replication/backup
ICS infrastructure status monitoring and defect detection
Procedure on instrument exchange
Procedures for power failure detection and handling
Hardware delivery to Subaru

## Slide 4: Items for review shown in ICS architecture diagram
Hardware
Pure-software
Individual
Integrated
Subsystem actor
Sequence (SpS/PFI)
Integrated control
Message Hub System (MHS)
Log/Status archive
Status viewer GUI
ICS Storage
Virtual Machine Infrastructure
PFS Network (PFS-LAN)
Backup infrastructure
TARGET AREA

## Slide 5
Status archiver
MHS
jsonp provider
SHM
Operational status viewer (browser)
database
DB to json
SQL
HTML
jsonp or CORS
summit
hilo
hilo outside-DMZ
DB
Summit master iSCSI storage
operation
backup
db server
DB
Hilo storage?
backup
db server
replication
Daily backup
Daily backup
External access
MHS
Status archive
(ICS)
operation
(on-site DRP)
Survey cluster?
Survey database
(On-site database backup/replication proposal)
Gen2
MHS
g2t
g2cam
m2t
IIC
MPS
MCS
MAC
MLP1
SAS
STS
Subaru
B/R/NCU1
ENU1
2
2
3
3
4
4
etc. …
DB
Storage
STARS
Hilo
On-site DRP
FPS
AGCC
TARGET AREA
TARGET AREA

## Slide 6: Overview of targets in this review
Network
  Design and its trade study
  Hardware had (almost) fixed, but some configurations are in discussion session
Link over fiber on telescope
  Design and on-site verification results
Storage and image data handling
  Design, item selection, performance verification
VM infrastructure
ICS infrastructure support hardware
Database server and its replication/backup
ICS infrastructure status monitoring and defect detection
Procedure on instrument exchange
Procedures for power failure detection and handling
Hardware delivery to Subaru
  Delivery schedule for preparation to accept each instrument component
Note: title pages are colorized for ease of seeking.

## Slide 7: Brief overview of PFS ICS design

## Slide 8: Instrument control system (ICS) overview
ICS is based on loosely coupled system design using MHS as message exchange server
  Every hardware control software module connects to the MHS (called as ‘Actor’), schematic diagram as below
    MHS provides client library for network communication and various message analysis and information handling
  External connections to telescope are managed by each dedicated module as Actor
  IIC – Instrument Interface and Controller Actor will handle entire system sequencing
From Subaru point of view, Gen2 is an integrated observation operation system to interface to telescope and instruments
  ‘g2cam’ library is provided for network communication handling
  ‘g2t’ will proxy between g2cam and MHS, but just as a bridge not as a sequencer
  Details in SSN-00016
Also, PFS need to have two more external connection to Subaru
  MLP1 – telescope control; PFS will receive and send error signal for Auto Guide (AG), details in SSN-00023
  STS – Subaru Telemetry System; official archive for telemetry and status
Gen2
MHS
g2t
g2cam
BCU1
RCU1
FPS
IIC
MPS
AGC
MAC
MLP1
SAS
STS
Subaru
NCU1
ENU1
2
2
2
2
3
3
3
3
4
4
4
4
etc. …
DB
Storage

## Slide 9: Instrument control system (ICS) data flow
Subsystems with camera generate FITS image file, these files are handled through storage
  Host (computer/VM) of actor mounts NFS shared storage, actor directly writs FITS files into NFS storage
    NCU up-the-ramp files (raw) are assumed into dedicated iSCSI LUN (direct mounted)
  Once actor finishes writing FITS file into NFS storage, actor push its filename as status
  FITS file transfer actor get event of status update with filename, actor push it to Gen2 via g2cam
    For auto guide, MAC will make special format image to be sent to V-LAN etc.
Some subsystems could use database server for saving/sharing configuration and/or status
  Assuming for Cobra related configuration and/or status
  Not planning to use for command/response of Cobra configuration itself
    But performance to handle several sets of 2500 points over MHS need to be tested (both server and client)
    In theory, these command/response/status will be distributed to all actors
Gen2
MHS
g2t
g2cam
BCU1
RCU1
FPS
IIC
MPS
AGC
MAC
MLP1
SAS
STS
Subaru
NCU1
ENU1
2
2
2
2
3
3
3
3
4
4
4
4
etc. …
DB
Storage
STARS
Hilo
On-site DRP

## Slide 10: Instrument control system (ICS) status flow
In addition to command and response over MHS, MHS supports handling of status
  Once each ‘actor’ pushes its status to MHS, MHS distributes it to all ‘actor’s
    MHS has a special repository for definitions of these status, each ‘actor’ need to register all of them as python dictionary
  On status distributed to ‘actor’, MHS client library analyzes status message, stores at local, and invoke event
  ICS has a service actor (SAS) to archive and analyze status
    Archive all distributed status into ICS database, and send summarized status to Subaru telemetry server (STS)
    Invoke warning message to engineer/operator based on pre-defined threshold
Gen2
MHS
g2t
g2cam
BCU1
RCU1
FPS
IIC
MPS
AGC
MAC
MLP1
SAS
STS
Subaru
NCU1
ENU1
2
2
2
2
3
3
3
3
4
4
4
4
etc. …
DB
Storage
Status archiver
MHS
jsonp provider
SHM
Browser (UI)
database
DB to json
SQL
HTML
jsonp or CORS

## Slide 11: Network
PFS has four IR detectors which make continuous data flow from devices to storage server(s), and its own camera system for auto guide. PFS instrument network shall be capable to handle these data flow with some burst-liked additions considered, and also is better to have capability for future upgrades of the instrument.
PFS plans to have its own network subnet with servers for DNS, DHCP, NTP. Network switches are planned to be managed under CDM (for modification of configuration, monitoring and alert handling), and also are monitored by PFS for instrument health checks during observation (e.g. to check network data flow for image data) and a data flow optimization.
This section is organized as follows:
L1-2 requirements and design
  This part includes cable or structure parts (so called L0)
  Performance verification is in next section – “Link over fiber on telescope”
  Handling on instrument exchange is in the last section – “Procedure on instrument exchange”
L3 requirements and design
Monitoring

## Slide 12: L1-2 Requirements – Network
Requirements from Subaru point of view:
Subaru standard recommendation of network switches
  Cisco 2960X-24TD-L or 2960CG-8TC-L is the standard (to keep management and spare handling simple)
  If other(s) is desired, Cisco 2960X, 2960CG or 3650 are possible selection
Network switch management
  Network switch shall be managed by and monitored from Subaru CDM
  Their configuration shall follow standard configuration (e.g. VLAN, remote access) of CDM.
  One VLAN ID will be assigned for PFS-LAN
Seemless access from Subaru network (incl Hilo, VPN) to PFS LAN for remote maintenance and operation are required, although security of instrument operation need to be secured in a required level.
All connections to the Subaru dome are in fiber connection.
Static IP address assignment is desired.
Requirements from PFS instrument point of view:
Required data flow rate
  CB2F – TUE-IR (SpS): (assuming) min 200Mbps for all IR detectors (one stream), currently on TCP but alternative is on UDP
  CB2F – Cs (MCS): not assuming real time data transfer, but raw stream in ~900Mbps
  PFS to Gen2 at CB2F: not well defined but as large as possible (item in discussion session)
Special requirements on numbers of fibers:
  PF or TUE-Opt – CB2F: two pairs of Ethernet, and two pairs of single mode fiber for PCIe bus extender

## Slide 13: L1 design – Network
Network switch selection
  PFS uses three places in the dome for its instrument. All connections between CB2F and three places are by fiber (as requirement), and no fiber connection is used for other parts – internal connection in one place. Considering required number of network fiber connections from CB2F, Cisco 2960X-24TD-L (24 metal, 2 SFP+) is not a good selection, and PFS will use 2960X-24TS-L (24 metal, 4 SFP) for CB2F and SpS network switches.
  A number of fiber connections at CB2F is at least 5 (or 7; depends on how much slack PFS will assume for detector data transfer), so PFS will use two Cisco 2960X-24TS-L at CB2F with dual FlexStack link – this is not for redundancy of network connections but just for capacity of network ports.
  Numbers of connections with large network data flow are limited, but most of them are originated from fiber connection. Also bandwidth capacity of FlexStack link is similar to backplane bandwidth (80G of FlexStack; 108G of switch with LAN Base). PFS will not set special assignments on port configuration.
Network connection
  Type of fibers for Ethernet connections is not one, but is a mix of SM and MM (62.5). Also distance between CB2F patch panel to three places are around 300m.
  PFS has selected 1000BASE-LX for fiber Ethernet links, to be capable of distances over fiber connections, and to make variety of SFP modules as small as possible.
  PFS will not use fiber connection within one physical place (as noted before), and all connections are by Cat5e or Cat6 metal lines.
  No port is configured as “shutdown”. Ports for VLANs other than PFS-LAN (e.g. Subaru management or V-LAN) are statistically connected, so all ports without media connection will be used only by PFS-LAN. To prevent confusion at on-demand connection, e.g. service ports on walls of SCR (spectrograph clean room), configure all temporary connection ports as PFS-LAN access ports.
External connection (to Subaru)
  External connection will use metal connection (1000Base-T). Connection for V-LAN is TBD.
  Currently PFS assumes one connection. (to be discussed in discussion session)

## Slide 14: Connection diagram / L1 design – Network
Notes:
This diagram does not show all connections, but just picks inter-place links and major devices.
Fibers marked as TBC are not yet at a stage of final assignment by Subaru.
Connection for iSCSI storage is under discussion (between iSCSI and FC).

## Slide 15: L3 requirements – Network
Requirements and conditions:
PFS LAN has assigned IP address range of 133.40.164/23 from Subaru.
Some of PFS ICS software modules and their configurations depend on hostname assignment from DHCP
  IP address is to be fixed to functions like BCU1-BEE but not to each device (handled by MAC address), and software configuration are selected using assigned hostname.
Some of PFS ICS hardware rely on BOOTP, and PFS wants to use DHCP option section for their configuration.
Some of PFS ICS hosts will be by virtual machines, MAC address assignment scheme is required.

## Slide 16: L3 design – Network
Design in PFS ICS:
PFS ICS will host dnsmasq server (DHCP + DNS)
  Network configurations are hosted in this server
  Two set of configurations are registered in git: MAC address and hostname, hostname and IP address
    On hardware replacement (broken or maintenance), only a set of MAC address and hostname will be replaced
    Hardware configuration is tracked by git hash, but this hash is not planned to be included in FITS header
      PFS will consider possibility to have some, if required (by PFS data reduction or by Subaru)
      (ToDo) Network block assignment need to be defined for ease of management (e.g. address block of 133.40.164.0/28 is for network switches)
  DHCP assignment for non registered MAC addresses will be enabled for temporary tools like maintenance or AIT
Critical boxes are by static configuration, e.g. network switch, VM host server
  “dnsmasq” server itself will be a VM client, its host shall be statically configured
  Even for static configured hosts, sets of configurations are registered into git
All ports except for up-/down- links are configured as access port
  PFS network is defined as one VLAN, but management network (or V-LAN) is also required
  Only up-/down- link ports to Subaru or between two PFS network switches are configured as trunk port
    If some host requires more than two networks (e.g. PFS-LAN and V-LAN), these shall have connections for each network

## Slide 17: Monitoring – Network
Requirements
Capable to monitor network connection and flow status both on demand and history
Capable to monitor switch health statistics
No special line or authentication for monitoring, use Ethernet connection
Design and implementation
Configure SNMP public read as “snmp-server community public ro” from all VLANs
Configure each port with name of peer
  Just for clarify, but name will appear on SNMP also, and status service does not need to have copied configuration
Traffic monitoring is recommended to be more than per a few tens seconds
  High frequency monitoring, e.g. per several seconds, is useful to detect spike/peak of network load
  1Hz SNMP readout worked on real hardware (ref: link over fiber on telescope section), but such high rate is not required
  Considering data store (or say, data volume to archive), statistics from high frequency monitoring is an option
    This is an option especially for status posted over MHS
  Visualization is a key for historical data, way is not defined yet. Could be done by STS, of course.
Weathermap could be a best option for display during operation, but not yet included in the plan
  Display in Gen2 might not be a good idea on data supply point of view.

## Slide 18: Monitoring – Network
Sample of network switch monitoring drawn by munin.
All panels are based on data acquired via SNMP. Traffic is by general IF-MIB plugin, others are by custom plugins. Statistics other than traffic are not changed frequently (CPU usage has some spike,,,) and frequent monitoring is not important.

## Slide 19: Link over fiber on telescope
PFS will use two types of signal for communication over fiber on the telescope between CB2F and places in the dome. One is Ethernet connection by 1000BASE-LX (1Gbps) over SM or MM fiber, and another is an optical PCIe bus extender with a USB host controller over SM fiber (4.25 or 8.5GBaud?). 1000BASE-LX is planned to be used to all three places, but an optical PCIe bus extender is only used between POpt2 (PFI in PFS) and CB2F for connection of USB devices to host computer at CB2F.
This section is to present a detail of technical requirements and limitations for each connections, trades and selection criterias, and performance verification.
This section is organized as follows:
Technical requirements and limitations
Trades and selection
  Selection of an optical PCIe bus extender was performed as a part of PFI, taking limitations on PFI side into account
Performance verification using real fibers
  Test procedure and verification results for 1000BASE-LX on TUE-Opt fibers
  Test procedure and verification results for PCIe bus extender on TUE-Opt fibers

## Slide 20: Requirements – Link over fiber on telescope
Ethernet connection
  Better to be the same component for both SM and MM fiber
  Fiber lengths are not short, and fibers itself are somehow old
    MM fiber will be used only for PFI connections
      High data flow rate is not required for this connection, ~100Mbps could be fine
      The highest bandwidth will be by COBRA FPGA communication, but low (or no) error rate is a key for COBRA FPGA operation
    Test and verify whether MCP is required or not for MM fiber connections
  Connection of CB2F – SpS will host continuous high data rate, but SM fibers are assignable for this line
Optical PCIe bus extender
  Space is quite limited at PFI side, selection is mainly limited by PFI design
  Need to be lined up between CB2F and PFI via real fiber
    Fiber assignment is possible for all SM, 50MM, 62.5MM
  Bus speed minimum requirement could be USB 2.0, but better to have more (e.g. USB 3.0) for slack
    Devices connected at PFI are six AG cameras, fiber back illumination system, monitoring camera and microphone, etc.
    Interface of PFS AG camera (FLI ML4720 MB) is USB 2.0, we will have six of them.
      Data rate from devices will not be large as ~1Gbps
      AG camera has ~3MB for full image, ~100Mbit for all but will not read as 10Hz
    PFS decided to divide these connections into two bus extenders, and to use bus extender with USB 3.0
  PFS PFI may not have enough space to have MCP along its cabling route

## Slide 21: Technical backgrounds – Link over fiber on telescope
Fiber cables on Subaru telescope have not replaced from its built (TBC). Run-length from CB2F patch panels are: (ref: OTDR measurement etc.)
CB2F – TUE-Opt IDF (PF Stand-by; so-called Route E): ~300m
CB2F – Ns-Opt IDF (route to TUE-IR/SpS; so-called Route F/G) : ~220m
  We will have additional b/w Ns-Opt IDF to TUE-Opt, but new fiber cable
CB2F – PF panel (so-called Route M): ~250m
Also we will need to attach fibers to switches on both sides, around 10m but with “new” fibers. PFS might not use Route E, and length of additional fiber to TUE-Opt on Route F/G will be shorter than 80m, we might be fine with assuming 225m + 50 (40+10)m fiber length between two SFPs.
Specific part # is unknown for fibers, but measured attenuation values are around 4dB (~3.8dB for GI62.5, ~4.3dB for GI50).
Messia III/IV system used SBus SIF card, and its specification seems like 1000-SX, but used around 300Mbps data flow max.

## Slide 22: Technical backgrounds – Link over fiber on telescope
Multimode (MM) fibers are categorized into several categories by minimum modal bandwidth defined at 850nm and 1300nm. Also per each category maximum link(-able) length for each application are defined, summarized as table below. FDDI and OM1 is for 62.5um, OM2-4 is for 50um MM fiber. Modal bandwidth is defined as -3db bandwidth on frequency spectrum of output light for impulse after passing specified length fiber.
As shown in table below, fiber with wider modal bandwidth can link longer length between transmitters. (Note; some max link length is limited per specification of communication protocol.)
category | MB (MHz*km) (850 / 1300 nm) | 1000-SX | 1000-LX (w/o MCP) | 1000-LX (w/ MCP) | 10G-SR | FC 1G | FC4G
 | (wavelength) | 850nm | 1300nm | 1300nm | 850nm | 850nm | 850nm
FDDI | 160 / 500 | 220m | n/a | 550m | 26m |  | 
OM1 | 200 / 500 | 275m | n/a | 550m | 33m | 300m | 70m
OM2 | 500 / 500 | 550m | n/a | 550m | 82m | 500m | 150m
OM3 | 1500 / 2000 | 970m | 550m | 550m | 300m | 860m | 380m
OM4 | 3500 / 4700 | 1040m | 550m | 550m | 550m | (n/a) | 400m

## Slide 23: Trades and selection – Link over fiber on telescope
1Gbps Ethernet
  PFS has selected 1000BASE-LX for its optical network
USB connection
  PFS has identified several items and performed on-site test
  Selected PCIe bus extender with USB host controller after on-site test
    Adnaco-H1A (photo below)

## Slide 24: Performance verification – Link over fiber on telescope
Performance verification was performed using real fiber at the prime focus of the telescope, for both Ethernet and USB extension. Since availability of real fibers at the prime focus is limited by day time works in the dome – the telescope need to be at the zenith for human access to fiber outlets, we also used TUE-Opt or Ns-Opt fiber patch panels for alternative test ports, whose fibers are also used by PFS for works at the standby (off telescope).
Performance test is performed by checking real data rate for full load supplied to each bus. Plans of measurements are developed for each bus, SNMP data transfer counter for network switches and dummy data read/write software for USB connection. For both buses, measurement plans are verified using short fiber cable connections, and system are verified with full load.
Connections are as follows:
CB2F
(OCB21)
PF or TUE-Opt
Cisco SW
SFP
SFP
LC-LC
MCP
LC-LC
MCP
Media Conv
Test PC
Metal RJ45
Test PC
Metal RJ45
Configuration for ethernet network test
PCIe extender
PCIe-USB
LC-LC
MCP; if required
LC-LC
USB Storage
Test PC
Configuration for PCIe extender (USB) test
MCP; if required

## Slide 25: Performance verification plan for Ethernet
Packet transfer error rate on switches could be gathered via SNMP (or other administrative methods) like 1.3.6.1.2.1.2.2.1.14 or .20 (also other values included transmitted packets, bps).
Using such switches and connects small computer(s) at both side, we can transfer large data flow and check network stability.
Reading status via SNMP in high frequency could make some load on switches, but not an issue for monitoring by 1-0.1Hz (already over requirement for our purpose).
Fiber communications are not affected with what kind of data is flowing, so we do not need special software for making data transfer, but we can just use netcat (nc). Use of “dd” or “rsync” (with –bwlimit?) was effected by short time performance degradation of storage, and was rejected.
Procedure is:
Place switches on both PF and CB2F, connect one or two PCs on both side
  We might not need full 1Gbps data flow, but better to check nearly conjection, so flow as much as possible without any limit
  Network is full duplex with two fiber cables, we don’t need to test two directions at one time
Check stability by monitoring status counters for full load (1Gbps)
  Pair of “nc –l –p XXXXX > /dev/null” and “cat /dev/null | nc X.X.X.X XXX”
  Gather data over ~100sec to check stability

## Slide 26: Plan verification – Performance verification plan for Ethernet
Used script to gather switch packet count
https://github.com/himorin/scripts/blob/master/network/ifmib_rate.pl
  Output status, flowed octets, error packets, discarded packets for in/out in specified second interval
Jitter of output period is measured as < 1msec with real cisco switch. (left below)
  Real measurement over 3000 points (in 1Hz) is shown
  Jitter in time domain seems random, so should not be serious issue on measurement
Data flow generation verification
  Data writing to NFS mount storage showed some sudden drop during test (middle below)
    Used SSD storage to gain write performance. No issue was found when write locally.
  Netcat data generation was succeeded as right below, first ~300sec is one direction, later is bi-direction
    Reason of periodical jitter (up and down in short time) is not clear but ~5Mbps for ~985Mbps.

## Slide 27
Test passed for all configurations with/without MCP. Bottom panels are samples of measurements.
1st: tested both with and without MCP on 62.5um MMF b/w CB2F and PF
  No change detected between with and without
  Checked laser dBm by cisco status (just to check difference between TX and RX)
    4.5dBm changed in average (-6.1/-1.7, -6.6/-1.9, -6.6/-2.7, -6.8/-1.6) = loss by fibers and connections
2nd: tested without MCP for all pairs b/w CB2F and PF on 50/62.5um MMF
  All pairs worked fine
3rd: tested without MCP for all pairs b/w CB2F and TUE-Opt (connector rack) on 50/62.5um MMF
  All pairs worked fine
PFS has decided:
Use 1000BASE-LX for all Ethernet connections over fiber
Changed MCP to be not a default plan
Results – Performance verification plan for Ethernet

## Slide 28: Performance verification plan for bus extender (I)
Finally selected device has limited capability for checking status of fiber link (as shown in figures below). If we find a way to check internal status of PCI Express bus, we could use these status to check communication failure rate, but it seemed difficult (or at least need to do some technical study).
Therefore, we planned just to check possible data flow rate, once we confirmed connection over a pair of fiber cables (TX/RX) by both LEDs and host computer operating system, and planned to compare with assumed maximum data flow rate – since its maximum communication data flow is kept as 2.5GT/s.
The PCIe extender had already tested with newly purchased 270m MM fiber at ASIAA and worked without MCP, prior to on-site test at the telescope.

## Slide 29: Performance verification plan for bus extender (II)
Procedure is:
Attach USB memories to USB hub at target.
  USB memory was tested at off-site prior to on-site test
  Two USB 3.0 memories were used to fill data flow
  USB SSD was not considered for this performance verification.
Run two tests, with short (~1m) fiber (local) and real
  Compare two results to check degradation by the real fiber
  Checked > 5min for stability
  Host operating system was Windows
    Used GUI storage performance measurement software for writing to and reading from USB memory
  Data rate and stability was checked using saved log file from software
    See next page for details
    At least one pair from assigned fibers are tested
      Fibers are validated by OTDR already

## Slide 30: Performance verification plan for bus extender (III)
Software used for test can output log into file. Format was as follows (sample cutout):
--------
[Test Start 4/28/2016 7:11:23 AM] drive: \\.\D: start_offset: 0 mode: Read blocksize: Auto type: sequential parallel: 1
blocksize: 64KB
result: 16000KB/s offset: 0% 8000KB
blocksize: 32KB
result: 13312KB/s offset: 0% 14656KB
: : : : :
result: 15872KB/s offset: 89% 27581120KB
[Test Stop 4/28/2016 7:40:59 AM] errors: 0 average: 15.3 MB
--------
First and last lines are start and end of execution, we take these lines to separate among tests. “errors” in the last line seems no unit, just take “0” as success (or graph go 0kB/s during error). Per each 0.5 sec one “result” line is written, kB/s is performance in the last 0.5 sec, and last kB is cumulative size of data tested. Blocksize seems size of block read/write, but haven’t checked its effect since size is well larger than packet size of USB protocol.
On USB 3.0 test, log file is only from one software, so we just memo (and get screen shot) their total data rate. And used this log file for checking long term stability and short-term degradation.

## Slide 31: Results – Performance verification plan for bus extender
For MM 50um fibers, connection itself had failed.
For SM fibers:
Achieved performance:
  Short length: ~180MB/s (~1.4Gbps)
  NsOpt (HDS): ~150MB/s (~1.2Gbps)
  Both are in total of two USB memories.
  Right graphs are for one of USB memory measurements (to show stability)
Communication was stable
  Although some load rebalance was observed over 5min test between two USB memories.

## Slide 32: Storage and image data handling
PFS ICS plans to have one central storage to cover all requirements over (most of) the entire instrument for both active and backup. Several exceptions exist such as local storage for MCS and MPS, MCS keeps intermediate image files at its local for operation and transfers them to shared storage on non-active phase, MPS has local data store (non database but binary typed file format; not tracked nor checked-out from git repository) for its operational configuration.
Also PFS has IR detector and plans to operate them in continuous readout mode, performance of storage and its connection (including storage server/services in ICS infrastructure) needs to be cared to match with required value.
This section is organized as follows:
Requirements
  Performance of storage
  Size of storage
Storage selection
Configuration plan
  Network connection
  iSCSI LUN organization
  NFS configuration and account
Performance verification
  Includes possible extensions
Monitoring and recovery plan

## Slide 33: Requirements (I) Performance – Storage
Requirements on storage performance is dominated by two client – detector data host, and database server.
Instrument detector data rates
  4 continuous stream from IR detector control computer
    Assuming 4k sq. image per 3-4sec, 60-90Mbps for one up-the-ramp
      Currently, changed to “per 5-6sec”, and ~50Mbps per one detector
      2.4TB/night for 90Mbps x 4 with 15hours operation per night, 36TB/run for 15day run
    Assumed no need to read up-the-ramp raw data from storage in short time over one exposure
      Protocol of IR detector readout is floating, better to have several options including tiered storage
  Only the final exposure of MCS FITS file will be immediately transferred to storage (and to Subaru)
    This transfer may not happen during IR detector up-the-ramp readout (ref. timing chart)
    Other files will be backed up during non-operation period or maintenance
  AG images is 1 or 2 x 2MB per a second (max), ~50Mbps max
Instrument operation
  VM images : client system itself will not require high bandwidth – disk IO is similar to ones at physical host
  Database : consideration on index, WAL etc. are required
In summary:
Read/Write performance
  600Mbps (50Mbps x 4SM IR up-the-ramp + 50Mbps AG + buffer) write performance
  Write mostly in sequence write (FITS data), ~10k IOPS is fine (or already over-spec?)

## Slide 34: Requirements (II) Size – Storage
Basic concepts on keeping data in on-site storage of PFS are:
Keep operational log data permanently
Backup strategy depends on targets
  Last (or a few) snapshots for incremental database, VM image
Image data up to half year (assumption)
  Mostly archived at Subaru, so we may reduce data holding period
Required capacity in summary: refer next slide for details
Capacity in total > ~100TB
  10TB for operational storage (e.g. VM, DB)
  10TB for backup
  80TB for FITS-liked data
    25TB for one run (15days) by uncompressed FITS files
    50TB to keep former runs
      Mostly raw up-the-ramp data
      Could be compressed after run -> 1/3 or 1/4; hopefully can keep 5-6 runs
      Seeking possibility to compress at the first moment

## Slide 35: Requirements (II) Size II – Storage
Data volume estimation in details:
Instrument detector data
  IR up-the-ramp data in ~200Mbps, 1.3TB/14h, 113TB for 6mo with 15days/mo
    Could be compressed after each run, and their size could be reduced as 1/3-1/4
    14h = 12h observation (avg.) + 2h calibration
    19TB for one run of 15days (at least this shall be kept in storage)
  CCD and IR (composed) FITS images are 50-100GB/night, 9TB for 6mo
  AG images are ~200GB/night, ~3TB/15days, 18TB for 6mo
    Focusing images are one order smaller
    These data could be important for instrument health evaluation point of view, better to be kept as long as possible
Operational data
  VM image : 30GB/client, 0.6TB for 20VMs, ~2TB for 3 generation backup
  Database : could not be on NFS, assumed to be direct iSCSI mount at database server host (physical or VM)
    Operation (Tron) log archive will be ~1TB over entire operation (ref. SDSS 15years in 500GB or so)
      Considering number of control items, this would be larger but not an order
    Survey and exposure execution database will be smaller than operation log
Backup
  Database backup can be in binary format, similar size as real one
    Backup for log database is enough with one snapshot
  Code and configurations are all in git repository, no need to have rsync-ed backup for ICS actor
    MPS configurations supplied from FPS are also tracked in database or as git repository
  No backup for image data

## Slide 36: Storage selection – Storage
CDS4004 with 120TB (or 108TB) iSCSI RAID6 4U storage server
  20D+2P+2H x 6TB NLSAS HDD, or 2x(9D+2P)+2H NLSAS HDD
  8x SFP(+) ports for data, 2x 1Gbps metal for management
    1Gbps metal SFP by iSCSI connection or FC (1,2,4,8Gbps)
      Mixable
      iSCSI ports are connected as device-multipath, but not bonded in network layer
Performance
  100K Read IOPS, 650K IOPS from cache
  6.4Gbps read, 5.3Gbps write
Host interface
  2U12 3.5in as one host or JBOD, up to 3 JBODs (+ 1 host)
    Using 1host + 1JBOD with fully populated disk (24 HDDs in total)
    Could add another 2 JBOD, if necessary during operation
  Two host controllers in redundant
    No battery backed-up cache, write from memory to flash by capacitor backed-up
  Max 8 SFP+, compatible with FC, iSCSI (hybrid) or SAS
Certifications
  NEBS 3 compliant for telecommunication
  ML-STD-810F/G

## Slide 37: Configuration plan (I) network – Storage
Requirements and limitations:
Maximum 8 connections of iSCSI (1Gbps metal) or FC are avail
  iSCSI ports are configured as device-multipath, no special configuration required at network switch
Considering possible configuration of VM nodes (for management?) with iSCSI mount, 2 or 4 iSCSI connection is required
  Like system log archive node, or database server
Connection ports at PFS-LAN CB2F network switch could be freely assignable
  Backplane (FlexStack connection between two switches) has enough bandwidth
  For management point of view, connecting all metal (iSCSI) connections to one switch is better and easy
NFS server is required in PFS ICS to proxy/expose storage
  1 NFS server could be enough, but better to separate operational one and image data storage
  FTP for transferring data to Gen2 could be required
Implementation plans:
Configuration I : all by iSCSI plan (current default plan)
  Simple configuration, iSCSI load will be balanced to all eight ports by device-multipath (depends on configuration)
  NFS storage server will have the same load to both RX and TX, performance and load balancing method need to be well verified
Configuration II : hybrid of iSCSI and FC
  Connect LUNs for detector image data storage by FC to NFS server
  Need to care of hardware redundancy (or backup connection port)
From next slide, configuration of connections and data flow for detector image data are shown for both configurations.

## Slide 38: Configuration I
Subaru core switch
Gen2 (storage)
PFS core switch
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
1x 1Gbps metal
8x 1Gbps metal
4x 1Gbps metal
4x 1Gbps fiber, for SpS
PFS NCU
PFS [BR]CU
PFS MCS
1Gbps fiber
2x C2960X w/flexstack

## Slide 39: Configuration I – data flow during exposure
Subaru core switch
Gen2 (storage)
PFS core switch
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
PFS NCU
PFS [BR]CU
PFS MCS
H4RG
CCD
Better to be tested

## Slide 40: Configuration I – data flow on CCD readout
Subaru core switch
Gen2 (storage)
PFS core switch
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
PFS NCU
PFS [BR]CU
PFS MCS
H4RG
CCD
Better to be tested

## Slide 41
PFS core switch
Subaru core switch
Gen2 (storage)
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
iSCSI FC
4x 1Gbps fiber, for SpS
PFS NCU
PFS [BR]CU
PFS MCS
1Gbps fiber
Configuration II

## Slide 42: Configuration II – data flow during exposure
PFS core switch
Subaru core switch
Gen2 (storage)
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
iSCSI FC
4x 1Gbps fiber, for SpS
PFS NCU
PFS [BR]CU
PFS MCS
1Gbps fiber
H4RG
CCD

## Slide 43: Configuration II – data flow on CCD readout
PFS core switch
Subaru core switch
Gen2 (storage)
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
iSCSI FC
4x 1Gbps fiber, for SpS
PFS NCU
PFS [BR]CU
PFS MCS
1Gbps fiber
H4RG
CCD

## Slide 44: Configuration plan (II) LUN – Storage
108TB storage (if we choose 2x(9D+2P)+2H configuration)
4LUNs or 8LUNs is planned
  1LUN or 5LUNs for detector storage, 80TB in total
    1LUN: one for all storage – CCD/IR detector, AG, etc.
    5LUNs: 4 for 4 IR detector controller, 1 for others
      This will make IR detector data handling complex (e.g. transfer to Gen2), and is an option when seriously required, like directly mounted from IR detector controller.
  1LUN for VM image storage and its backup, 3TB in total
    Including revision history
    VM image could be in qcow2 for incremental host backup, but default plan is raw image
  1LUN for operational NFS storage and backup, rest of all
  1LUN for PostgreSQL database, 3TB
    Directly mounted from host or VM of database server
    This could be better for file IO on filesystem side (really?)

## Slide 45: Configuration plan (III) NFS – Storage
Basic plan for NFS are:
Export configuration: async, wdelay, no_subtree_check
  Async could have some issue on system failure, but it should be safe since our backend is redundant storage server.
Pre defined accounts for system and operational
  Some system accounts need to be defined (pair of name and id), such as libvirt, postgres
  Operational account (e.g. to run actors) is united as pfs/id=1000
  User accounts could be defined, LDAP or some account database are desired
    Need to verify configuration and performance for NFSv4 and LDAP if we want to go NFSv4
Storage format need to be defined considering its performance in combination with NFS server.
  Currently assuming jfs for small file regions where file stat access is large, xfs for large data file regions.
    Refer notes in performance verification section.
  But still TBD.
Mount positions are managed in ‘datamodel’
  Not yet fixed for the name of directory, but full path shall be in ‘datamodel’ definition.

## Slide 46: Performance verification – Storage
Planned performance verification is in two stages:
To check maximum bandwidth with simple configuration
  Configuration: Use the similar network topology and the NFS storage server
  Aim: List possible drawbacks to configurations and/or performance optimization on storage and data flow
To check capability for real operation and level of slack with semi-real configuration
  Configuration: Use configuration similar to the real one as much as possible, including detector simulator and other storage dependent devices
    Need to estimate possible load to the database system
    Also add some dummy module to generate random storage load for measurement of slack
  Aim: To verify the entire system works well, and to check how much slack the system has (needless to say; its ratio is quite important for stable operation)
    Also to check effects from random IO to the entire system, such as VM disk image, database system
PFS did the first stage successfully with the real storage server and computer device for NFS server.

## Slide 47: 1. Background – Performance verification – Storage
In PFS instrument at summit, we have several detectors which output large volume data: IR detectors and CCDs at spectrograph (SpS - spectrograph system at TUE-IR or so-called IR4), metrology camera (MCS) at Cs, and cameras in PFI (AG is connected through dedicated optical link of USB and controlled at CB2F; fiber viewing camera and central camera is small and will not be used in normal situation). For spectrograph, we have four 4k sq. IR detectors in ~3-4sec per frame readout speed, which is ~360Mbps for 3sec per frame, ~270Mbps for 4sec per frame in total (if 300kHz with 32port, readout time taks ~1.7sec and data rate will be ~615Mbps in total of four cameras), and one order smaller data rate from CCDs. Metrology camera is 50M pixel detector which output one frame per 0.8sec and ~1Gbps (100MB/frame in 0.8sec) in video streaming mode (TBC) is assumed, but normally data will be written only to local storage and final shot per each configuration stage will flow from Cs to CB2F. AG is controlled at CB2F and data rate for other devices are small. Network and storage configuration is required to match with these requirements.
Network configuration of PFS-LAN is to have two switches at CB2F as core switch (calling as "core" even its switch is not a level in standard definition, but as a terminology of three layered switch configuration), to have one switch at each focus (PFI, Cs, SpS) as distribution switch. Between CB2F and SpS, four 1Gbps SM links are used as LACP. To PFI and Cs, only one fiber links per switch is connected. Two core switches at CB2F are in a stack connected by flexstack dual link and are almost considerable as one big network switch.
PFS storage has eight 1Gbps metal links to the core switch and requires iSCSI device multipath configuration for load balancing over links at initiator.
Originally, PFS assumed to have detector control computer(s) for IR detectors at CB2F with network connection to detector control electronics, and FITS files were assumed to be written by these detector control computer(s) at CB2F. That keeps data connection between CB2F and SpS for IR detector readout as four single peer to peer connection, and all data generation and transfer after detector control computer(s) within CB2F where we can have more free options on network and computing resource configuration.
After some technical evaluations and discussions, PFS now have IR detector control computers at each camera (so-called "BEE" computer; small card typed PC/104), and these computers write FITS files to iSCSI storage (direct or via NFS). If we configure as these detector control computers (BEE) to mount iSCSI storage (LUN) directly, one LUN is possible to be mounted from one initiator, we need another connection to NFS server on these detector control computers. So, having NFS host server(s) at CB2F and have connection to the server(s) from these detector control computers is the only possible way.

## Slide 48: 1. Configuration – Performance verification – Storage
For first stage, we only evaluated storage performance by block/stream IO from multiple data generator hosts. Host computers are:
Data generator (4 PCs): 4C8T Corei7 with 16GB memory, one 1Gbps metal interface
Host server (1 server): 4C4T Xeon (E5310) with 9GB memory, four 1Gbps metal ports
These hosts and a storage server are connected to network switches in the similar configuration as at the summit:
CB2F.cisco 1/0/25-28 - SpS.cisco 1/0/25-28, connected with four SM fibers (1000BASE-LX) in LACP
CB2F.cisco 1/0/1-4 - host server eth2-5 (as bonding; configuration on Linux side varies for measurement)
CB2F.cisco 2/0/1-8 - iSCSI storage eight ports
SpS.cisco 1/0/9,11,12,13 - four data generator(s) in 1Gbps metal each
Monitoring of system performance is done by both host performance counters and also network switch monitors via SNMP.
CB2F 2/
CB2F 1/
SpS
FlexStack
(dual)
1000B-LX
(4 in LACP)
Storage
NFS server
Data generator
Data generator
Data generator
Data generator
1Gbps metal x8
1Gbps metal (x4 in LACP)

## Slide 49: 1. Results (I) – Performance verification – Storage
Before testing storage performance, we checked network performance with several possible configurations. Test was performed as the same way as one we did at the summit for fiber link, by “nc IP port < /dev/zero” with data flow from data generator computers to the NFSv3 server, and performance monitoring by SNMP status monitoring.
Points to be configured is bonding configuration on NFS server (Linux), and LACP operational configuration on LACP link between CB2F-1 and SpS switch is kept as
port-channel load-balance src-ip
channel-protocol lacp
First one can have other value, but these will not work or will be the same as “src-ip” in this configuration with small number of devices connected, so we have not tested.
Results are:
802.3ad for bonding: data rate was at 3.94Gbps in total for optimized IP address assignment
balance_rr for bonding: data rate drops to 1.1Gbps (switch configured port as stand-alone)
  This could be overhead of round robin routine.
balance_alb for bonding: ~30% degradation happened from 4Gbps (in 802.3ad right before) to ~2.9Gbps
Note:
balance-rr: transmit in round robin, receive is decided by switch in connection, but normally switch will set ports as standalone and receive will be similar to transmit.
balance-xor: transmit in xor based balancing, receive is decided by switch in connection
802.3ad: LACP, in xor based balancing policy
balance-tlb: transmit in balancing based on current load of network link in bonding (or configurable to xor based hash policy), receive is decided by switch in connection but normally the current network link (used in transmit) will take.
balance-alb: similar to -tlb with receive in round robin based on ARP negotiation. This mode uses ARP replies for selection of network link to be used in receive, and will take some time delay on load balancing (re-)configuration, Calculation on load balancing (xor) is selectable from MAC address or both MAC and IP address.
  calculation is done in: (<source_MAC_address> XOR <destination_MAC>) MODULO <slave_count> (((<source_IP> XOR <dest_IP>) AND 0xffff) XOR (<source_MAC> XOR <destination_MAC>)) MODULO <slave_count>

## Slide 50: 1. Results (I-b) – Performance verification – Storage
Notes for real operation from trials and results with this configuration:
We had several trial to have good load balancing over LACP, to assign four data flows to four fiber links in one per one. We can test load balancing parameter on terminal as:
  cb2f#test etherchannel load-balance interface po1 ip 0.0.0.0 10.100.200.241
  Would select Gi1/0/28 of Po1
(note: port-channel 1 has gigabitEthernet1/0/25-28), and I got following selections for 0.0.0.0-0.0.0.15 (in sequential)
  28, 27, 25, 26, 25, 26, 28, 27, 25, 26, 28, 27, 28, 27, 25, 26
Results for other port channel or another switch with the same IOS version were the same. This could have some impact on the real IP configuration, and also need to be kept in mind.
Especially, we cannot control MAC address of PC104 devices, and also we assume to exchange PC104 board to spare on device failure with keeping assigned IP address (IP address is issued against service but not to device), LACP load balancing by IP address is safer option to keep things well under our control.
Since output of calculation for load balancing was the same over two switches and three port channel configurations, I suppose it is fine to assume the same balancing configuration over more than two LACP connections from IR detector control computer at SpS to NFS server at CB2F. Data flow in large volume from SpS to CB2F is only one direction for all switches in between, so load balancing on cisco switches are fine with configuration to refer src IP addresses (or dst-src-ip if we need).
For iSCSI storage and NFS server, we do not need load balancing configuration on network layer (switch or network interface of Linux) since our iSCSI storage has eight network links and can balance well on device multipath layer. Also resource is not limited at CB2F, that we can increase number if in emergency for normal operation, we may not encounter such difficult situation on load balance configuration.
Connections of CB2F-SpS and CB2F-NFS server are only possible ones with LACP (or some option of Linux bonding), so we do not need to put destination IP address for load balancing calculation, which may make our situation simpler for selection of pair of src-dst.
Also this will make some difficulty on data flow between PFS and Gen2 for large FITS files transfer, we need to check and evaluate in simulating the configurations.

## Slide 51: 1. Results (II) – Performance verification – Storage
Storage performance was measured with two configurations for bonding interface of NFSv3 server, using simple data writing of 1TB continuous file by dd from /dev/zero not to introduce any performance degradation at data generation side.
NFS configuration was rw, async, wdelay, no_subtree_check, sec=sys, no_root_squash, no_all_squash
Configuration I: round-robin
  path_selector=“round-robin 0”
  rr_weight=priorities
  Total bandwidth was 1.72Gbps, and almost uniform distribution (within ~5%) over eight iSCSI connection from NFS server to storage was observed
Configuration II: layer3+4
  2.33Gbps from 4 data generators, almost in uniform distribution
  One data generator occupies one connection in 4 LACP bonded connection between switches
Notes:
We already have found some issue with NFS over xfs region for performance degradation on file node (and metadata) manipulation, compared to NFS over jfs. We may not use xfs for the real configuration.
We already have found performance degradation with jfs storage when we write a file more than 1TB in sequential append mode, which does not happen with xfs storage in the same hardware and operating system (Debian Jessie) configuration. PFS does not plan to use large files more than 1TB, we do not have any plan to find any mitigation on this issue.

## Slide 52: 1. Results (II-b) – Performance verification – Storage
Also we have measured basic storage performance over NFS server from data generator computer. Results were followings:
bonnie++ @ /mnt/iscsi/bonnie from is0
Version 1.97 ------Sequential Output------ --Sequential Input- --Random-
Concurrency 1 -Per Chr- --Block-- -Rewrite- -Per Chr- --Block-- --Seeks--
Machine Size K/sec %CP K/sec %CP K/sec %CP K/sec %CP K/sec %CP /sec %CP
is0 31920M 2119 97 111498 4 47356 5 5500 90 105527 4 1411 24
Latency 8188us 200ms 15121ms 24703us 341ms 1113ms
Version 1.97 ------Sequential Create------ --------Random Create--------
is0 -Create-- --Read--- -Delete-- -Create-- --Read--- -Delete--
files /sec %CP /sec %CP /sec %CP /sec %CP /sec %CP /sec %CP
16 2355 15 +++++ +++ 4221 13 2412 14 7834 15 4425 14
Latency 1282us 17292us 19694us 1718us 572us 665us

## Slide 53: Monitoring and recovery plan – Storage
The target storage server can issue alerts on system events by:
SNMP trap (target port is fixed)
Email (SMTP server is required)
Syslog
PFS plans to cover all three notifications, and to use SNMP trap (via a proxy to MHS) as real time notifications at panels for operators and email for maintenance operations.
All components in the storage server are redundant, that CPU module and power (per single 2U unit) are dual and HDDs are in RAID6 with one hot spare per each unit. This makes recovery operation not to be an emergency, and later maintenance work is enough (including lead time for getting spare parts from vender – all devices including HDDs or SFPs are vender locked).

## Slide 54: VM infrastructure

## Slide 55: ICS infrastructure support hardware

## Slide 56: Space condition of PFS CB2F rack
Functional requirement from PFS
  Can mount 30” (~760mm) depth computer
    PFI/MPS control computer (Dell Precision R5500) is ~30” depth 2U
  Can mount 0U PDU at rear side
  Want to have 42U
  Power input by NEMA L5-30P
Subaru standard
  External cabling will be from floor hole
  No forced cooling (TBC)
Assumption
  No redundant power supply

## Slide 57: Unit registration – overview
(TBC) U in total
  Management and service resources
    0U PDU
    1U KVM
  System wide infrastructure
    2x 1U Cisco network switch (rear side??)
    1U patch panel
    UPS is TBD (will not?)
  IIC computing resource
    2x 2U iSCSI storage
    3x 1U computer (TBC)
  PFI control
    ?U AGCC host computer (extender fiber connection to PFI)
    2U MPS host computer
  SpS control
    Originally assumed to have 2-4U computer for IR readout, but will not (TBC)
  No need for Cs (MCS)

## Slide 58: Management and service resources
PDU
  0U vertical mount type / ATEN PN7320
  20 port outlet, 2 line breakers
  2 sensors (1 temperature, 1 temperature + humidity)
  Vendor manual
    https://pfs.ipmu.jp/docsrv/doc/Software/ICS/ATEN%20PN7212-7320%20PDU%20user%20manual
KVM
  1U 16port KVM / ATEN KN2116A
  Vendor manual
    https://pfs.ipmu.jp/docsrv/doc/Software/ICS/ATEN%20KN2116A%20KVM%20user%20manual

## Slide 59: System wide infrastructure
PFS-LAN core switch
  2x 1U Cisco 2960G connected by FlexStack
    Not separable on mount
  Mount toward rear??
1U patch panel
  With cable feed through from front to rear?
  AUX metal ethernet at front (TBC)
  Fiber patch panel at rear?
    Connection exchange of PFI fibers
UPS
  TBD
  2-3kVA in 2U could be enough?

## Slide 60: Database server and its replication/backup

## Slide 61: Status monitoring and defect detection

## Slide 62: Procedure on instrument exchange

## Slide 63: Procedures for power failure detection and handling

## Slide 64: Power failure mode I - glitch
“glitch” is actually not a power failure, voltage will not fall down to 0V, but will be effectively low voltage (normally to 80% level in Japan) for short time up to ten cycles.
This mode will not happen UPS-ed power line, like PF (POpt2) and Cs
  TUE-Opt stand-by backed up by UPS-2 (+DG)
  UPS-2 (+DG) and DG (w/o UPS) on SpS (IR4 = TUE-IR), FMOS is on UPS-2 (TBC)
    (TBD/TBC) PFS would bring backup-UPS for SpS placed at IR3
  Ctrl. Bldg. 2F is backed up by UPS-3 (w/o DG) (or we also bring our own, as others)
Situations / fatal events will be happen
No impact on observation – telescope will continue working
Need to continue instrument operation – regardless modes (exposure, configuration)
Actions / considerations required
Check power line quality (glitch) - underway

## Slide 65: Power failure mode II – several minutes
As for telescope operation, power failure of several minutes level will be covered by dome-UPS (UPS-1 and UPS-2; CVCF), but dome rotation and tracking will stop. Instrument need to be operated without failure, but “active” operation like exposure or moving parts need to be finished or suspended as soon as possible after power failure detected.
Situations / fatal events will be happen
Dome co-rotation and telescope tracking will stop
Dome-chiller will down until diesel come up
Actions / considerations required
(Bring PFS-UPS for SpS)
When to give up this mode, and to switch mode III (next slide; start shutdown)
Operations to be taken
Stop exposure – close shutter, read detector
Turn off illuminators – fiber back illuminator (science, fiducial), calib. lamp etc.
Stop fiber configuration procedure
Keep PFS backend (infrastructure) functionality until FITS finalized if under exposure
Stop AG camera for thermal protection (no glycol flow to HEX)

## Slide 66: Power failure mode III – ten-odd min to several tens of hours
After diesel generator (DG) came up and stabilized, MDB-2 will run with DG power. Dome chillers (in operation after DG supplied) and some part of telescope (drives on) will remain in operation, others like dome air compressor will be off to reduce load on DG.
Situations / fatal events will be happen
Instrument control computers (CB2F) had gone
  No control on PFI
Dome chillers return on diesel came up (hopefully)
Operations to be taken
PFS ICS infrastructure at ctrl. bldg. 2F need to be down before this mode
  PFS-LAN, shared storage, database server, heartbeat system will down
  MHS VM (+ e.g. telemetry archive) need to start running on SpS infrastructure
Subsystems are operated in stand-alone mode
  shutdown non-emergency items
  Turn off outlets of PDU – for required by control box, e.g. ENU control box
Monitor dome chiller glycol supply temperature at SpS chiller

## Slide 67: Power failure mode IV – more than several tens of hours
Diesel backup will go away after several tens of hours from power failure. PFS need to shutdown all subsystems before it.
Situations / fatal events will be happen
All power will down
Actions / considerations required
Emergency telemetry logging system required??
  IR detector warm up heater
  Telemetry logging into writable storage on PC108, but need to be reliable on rw
    Lifetime of SD card is not so large w/ massive write
Who (system) to decide to shutdown? – need control at SpS floor
  No way to get diesel status? e.g. remaining time. DG down will be detected w/power.
  PFS-UPS at IR3 will be for shutdown, batteries in racks for keep heaters and PC108 on.
Operations to be taken
Shutdown control computing resources
Stop cryo-cooler, warm-up detectors by heater (TBC)

## Slide 68: Subsystem shutdown procedures and remarks
Before listing shutdown procedure, conditions are follows.
PFI
  No UPS within PFI, rely on system power supply through cable wrapper
  PDU exists but only several ports
Cs/MCS
  No UPS, PDU within Cs/MCS
Ctrl. Bldg. 2F
  Rack mounted UPS (TBD) and 0U network-PDU for PFS ICS rack
SpS
  Two operational conditions
    Dewar not cooled down or cooling down to operational temperature
    Dewar cooled down at operational temperature
  Rack sized UPS to cover SpS power until diesel coming up
  Network-PDU for infrastructural computing/network resources

## Slide 69: Subsystem shutdown procedures and remarks I - PFI
No battery within PFI, PDU is not for shutdown procedure but mainly for trouble shooting.
AG camera + USB-Opt converter could be down w/o command
  (TBC) AG camera will be heated up without cooling by glycol (stops until DG up)
COBRA system at not queued could be down w/o command
  Note, check FPGA condition on power on/off
COBRA system under queued need to be finished
  e.g., do not issue next queue from MPS to FPGA
Back illumination, camera could be down w/o command
  But still need to be down for thermal issue
Possible procedure
Stop cameras and illuminators, if required (TBC)
Wait to finish executed queue to COBRA system
and shutdown (or wait for power to disappear)

## Slide 70: Subsystem shutdown procedures and remarks II – Cs/MCS
No buttery nor PDU at Cs/MCS, excl. diesel and UPS-2
Control computer need to be shutdown by OS
CMOS camera and controller could be down w/o command
Mirror motor could be down w/o command (need to be confirmed)
Possible procedure
Shutdown control computer, on moving to stand-alone mode

## Slide 71: Subsystem shutdown procedures and remarks III – CB2F
Control building 2F (CB2F) is backed up by UPS-3 but without diesel. PFS will bring PDU, UPS of PFS dedicated need to be considered depending on timing, since we will have key infrastructural modules for operation at CB2F and need to care on procedure. (5min to finish, is short??)
Key modules
  Network switch : if down, we cannot reach to subsystem
  Storage server, database server, heartbeat system, VM server, MHS server
Operational modules
  Subsystem controllers : IR SAM control, AGC, PFICS, MPS
  System modules : IIC (master sequencer), logging system, Gen2 connection system
Possible procedure
(decided to move mode-III, and to start shutdown procedure)
Wait to finish subsystem commands – FITS finalization, COBRA operation, lights off
Shutdown operational subsystem modules AND send “standalone” signal to subsystems
  (after hardware operation finished; but shall be finished within “decision” period)
  IR SAM / CCD-BEE control : readout, finalize up-ramp to FITS files + sending to Gen2
  PFICS, MPS : stop by commanded COBRA move finished
Shutdown system modules : IIC, logging system, Gen2 connection system, MHS server
  Live migrate MHS and logging system to SpS control box
Shutdown infrastructural computing resources (servers) : VM, database, storage
(TBD) Make network switch remain operation, until UPS power down

## Slide 72: Subsystem shutdown procedures and remarks IV – SpS (I)
Procedure for SpS will depend on status of dewar cooled down. If dewar is in operational temperature (e.g. 88K for IR detector), we shall keep cryo-cooler as much as possible. Items other than dewar, spectrograph need to stop its operation on power failure detected.
(TBC; issue resolved or not) For whole shutter system (incl. computing), we need to keep power backed-up by UPS during detector readout, since it will automatically open/close on power-on.
If SMx/yCU is not in operational temperature
  any operation on the dewar will be stopped – vacuum, cooling.
  Vaccum to dewar will be closed by emergency stop valve?
    (TBC) will we cool down dewar while turbo pumps on? (the last bulb to dewar open)
If SMx/yCU is in operational temperature
  need to maintain their temperature as long as possible.
  (TBC) need to keep xCU/BEE and PCM (VCCS) on to monitor telemetry
  PFS-chiller is better to be operated while cryo-coolers are on. – even dome chiller down by trouble? (TBD)
  better to have an emergency heartbeat system at SpS floor (after “standalone”)
After (final) shutdown commanded, dewars (detectors) are possible to go environment temperature, but heaters are required (not only for H4RGs but also on CCDs).
Considerations required
PFS-chiller could be backed up by PFS-UPS before diesel up? Also could be backed up by diesel?
  No. Need to down PFS-chiller, since dome-chiller downs. Reserver will work during this period.
Heartbeat system dedicated to SpS is required during “standalone” period?
Need consideration on storage for BEE (PC104 in readonly storage)

## Slide 73: Subsystem shutdown procedures and remarks IV – SpS (II)
Possible procedure
Right after power failure detected, IIC shall command to subsystems
  Stop exposure, close shutter and readout detectors
  Stop illumination sources – back illumination, internal illumination, fiber monitoring
  Stop non-operational dewars – vacuum, cryo-cooler
Shift to “standalone” mode
  Shutdown non-emergency computers
    ENU controllers (LAM), fiber monitoring system (LNA)
    IR H4RG SAM – if we cannot just power disconnection
  (TBD) shutdown SCR environment control
  Start SpS emergency heartbeat system and MHS+ run on SpS computers
“shutdown” mode
  Shutdown cryocooler, (ion-pump : at when??)
  Shutdown xCU/BEE PC108, xCU VCCS (PCM)
  Network core switch will down at diesel down
  Make xCU/BEE PC108 standalone, turn on heater.

## Slide 74: Subsystem startup/recovery procedures
Once PFS started sequences for power failure, control systems will be in irregular state than normal power on/off procedure. Also power supply may be back suddenly before instrument checked by operator, we need to be care of hardware safety conditions with disabling power supply before power cut procedure and so on.
Detailed studies are required for all subsystems, following are examples.
SpS xCU ion pumps and cryo-coolers
  Should not be operated before vacuumed and glycol temperature in normal
PFI AG cameras
  Should not be operated before glycol temperature in normal

## Slide 75: Operational flow on each power failure mode
Power failure detection
  Will follow “official” procedure of Subaru, also we have some mechanism via UPS etc.
Immediately after power failure detected
  Stop operational commands in execution
  Close shutter and readout detectors, finalize data (CCD/IR)
Decision to switch to subsystem-level stand-alone mode
  After operational commands finished
  CB2F controllers need to be successfully shutdown before UPS out
  Staged switch could be possible – depends on timeline
    First, shutdown subsystem controllers , whose start-up time is short
    Telescope may not be recovered immediately after power recovered, we have time
Subsystem-level stand-alone mode
  PFI have no controller, Cs/MCS could be down right after stand-alone mode
  SpS need to change operational mode (shutdown un-emergency items)
System shutdown (final)
  SpS subsystems will be the one

## Slide 76: Operational flow on each power failure mode - timeline
Power outage
UPS-3 active
UPS-1,2 active
diesel active
dome chiller down
Decide to standalone
Decide to shutdown (SpS)
UPS active @ CB2F (UPS-3 or PFS-UPS)
Finish COBRA operation
Finish detector operation
Subsystem @ standalone
PFS-LAN down
Stop AG
Stop illuminators
SpS cooling active
Detectors warm up
Shutdown MCS computers
Shutdown subsystem controllers @ CB2F
Shutdown system modules
Shutdown CB2F physical servers
SpS-chiller non-backup by dome-chiller
Stop turbo pumps
Stop exposure, exec readout
Shutdown ENU, FMS
Start SpS emm heartbeat?
Shutdown SCR
Shutdown cryocooler
Standalone xCU PC108
Event + 5-10min
Event + 1-3days

## Slide 77: Hardware delivery to Subaru

## Slide 78: Items and assigned delivery
Followings are hardware items which the project (or Subaru) need to prepare or deliver to the summit, and subsystems use these items.
CB2F (Control Building 2F)
  Rack to host items (Subaru): before all of followings
    Assumed deepest unit is ~760mm (MPS), ~650mm (DB host)
  Network switch (IPMU; already in hand): (at least) 1 at MCS, 2nd at SCR
  ICS RAID6 storage (IPMU; already in hand): SM1
    MCS backup could be done with small storage?
  VM host computers (IPMU; some already in hand)
    (at least) 1 at MCS (any subsystem delivered to summit) – to run MHS
    Others depends on system load
  Serial communication (MLP1; IPMU) host: PFI
  KVM, PDU etc. (IPMU; some already in hand): MCS?
  DB host (IPMU; spec TBD): SM1??
SpS (both IR3 and TUE-IR)
  5th rack (from JHU): SCR
  Network switch to connect CB2F (IPMU; already in hand): SCR
  UPS and power supply (Subaru): SCR
  1U host computer @ 5th rack (IPMU; spec TBD): SCR
  Telemetry devices/system (TBD): SCR (or SM1)

## Slide 79: Setup to accept MCS
MCS will be installed as Cs instrument. We need to have minimum operation hardware at CB2F, including PFS network.
19inch Rack (Subaru)
PFS network switch (at least 1; IPMU; already in hand)
  Also connection to subaru’s core switch
VM host (IPMU; 1 already in hand)
  Hosting administrative VM, e.g. dnsmasq
KVM, PDU (IPMU; already in hand)
At this stage, no special care for power distribution is required, only like connecting things to PDU at CB2F. Also network is simple, we need two fiber connection to Cs and its standby (one active, one backup), one connection to subaru core switch with routing.

## Slide 80: Setup to accept SCR
In parallel to build SCR (Spectrograph Clean Room) at TUE-IR (IR4), we need to have control hardware for SCR.
2nd network switch at CB2F (IPMU; already in hand)
  might only need 1 SFP to SpS, but better to have and check working at this moment
Network switch at SpS (IPMU; already in hand)
5th rack (from JHU)
UPS at IR3, with power distribution/panel (Subaru)
1U host computer (also for SCR control) (IPMU)
Telemetry devices (TBD)
  e.g. Lakeshore temperature monitor and sensors
At this point, we need full power distribution system to supply spectrograph, both UPS and power panel w/ cables. Environment active control subsystem for SCR shall be considered as a part of SCR, so not listed here.
For network and storage, we only need “connected” at this point, so performance evaluation on network in parallel to SCR preparation (or validation) is fine.

## Slide 81: Setup to accept SM1,2
Before we have SM1,2 at summit, we need almost all of hardware.
ICS RAID6 storage (IPMU)
DB host (IPMU)
  Not as full operation (e.g. interaction with ETS or survey coordination), but to store MHS status archive or telemetry etc.
Before this point, PFS network and storage need to be fully prepared and validated on performance point of view (for NCU1,2 operation).

## Slide 82: Setup to accept PFI
Most of computing and power resources need to be active well before delivery of PFI to the summit.
Serial communication (IPMU)
  This communication will be validated at factory of melco (Mitsubishi; at Amagasaki) in test setup.

## Slide 83: Discussions on interfaces between Subaru and PFS
Network connection to Subaru (data flow, V-LAN)
Access control to/from PFS network
System alert handling (items to STS)
Engineering data archive (during on-site AIT, independent unit test)

## Slide 84: Discussions I – Network connection to Subaru
Pass multiple VLAN to PFS network switch through uplink (as trunk port)
  PFS-LAN, V-LAN, CDM management LAN
  Note, V-LAN network is required to be limited as 100Mbps
Larger bandwidth connection to Subaru network
  Like, multiple 1Gbps metal connection in LACP, or 10Gbps fiber connection
  Faster data transfer if we archive composed up-the-ramp data
  Depends on target host configuration of g2cam

## Slide 85: Current plan – connection configuration
Subaru core switch
Gen2 (storage)
PFS core switch
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
1x 1Gbps metal
8x 1Gbps metal
4x 1Gbps metal
4x 1Gbps fiber, for SpS
PFS NCU
PFS [BR]CU
PFS MCS
1Gbps fiber
2x C2960X w/flexstack

## Slide 86: Plan second? – connection configuration
Subaru core switch
Gen2 (storage)
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
1x 10Gbps fiber
iSCSI FC
10Gbps metal/fiber
4x 1Gbps fiber, for SpS
PFS NCU
PFS [BR]CU
PFS MCS
1Gbps fiber
C2960-TD
C2960-TS
flexstack

## Slide 87: Plan second? – during exposure
Subaru core switch
Gen2 (storage)
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
1x 10Gbps fiber
iSCSI FC
10Gbps metal/fiber
4x 1Gbps fiber, for SpS
PFS NCU
PFS [BR]CU
PFS MCS
1Gbps fiber
C2960-TD
C2960-TS
flexstack
H4RG
CCD

## Slide 88: Plan second? – on CCD readout
Subaru core switch
Gen2 (storage)
PFS iSCSI Storage
PFS NFS server
PFS SpS distribution switch
1x 10Gbps fiber
iSCSI FC
10Gbps metal/fiber
4x 1Gbps fiber, for SpS
PFS NCU
PFS [BR]CU
PFS MCS
1Gbps fiber
C2960-TD
C2960-TS
flexstack
H4RG
CCD

## Slide 89: Discussions II – Access control to/from PFS network

## Slide 90: Discussions III – System alert handling

## Slide 91: Discussions IV – Engineering data archive

## Slide 92
Backup or copied materials to be used

## Slide 93: Updates/Progresses – shared infrastructure
Communication fibers at Subaru have tested and passed
  Mostly by real data flow, except for 1Gbps SM fibers (OTDR)
ICS storage performance have verified with simulated 4 H4RG data streams
  Simulation configuration: Storage – NFS server – 4x data generator
  Achieved ~2.3Gbps file write, enough for 4 H4RG data streams
  ToDo
    Need some consideration on network configuration
    More realistic test (e.g. having both read/write) could be better
PFS-LAN network host stage for configuration and stability passed
  Using real hardware to be used on-site
  Some management configuration will be modified by Subaru (CDM) after delivery
  ToDo
    Connection between PFS-LAN and Subaru network is not fixed yet
Data backup procedures (e.g. DB) are in production at pfs servers
Virtual machine servers for ICS components are under host stage at IPMU
  Dell R710 (2U Xeon E5506) x2, R410 (1U Xeon E5640x2) x3, R310 x1+ backup (2U x2)
  4 port Gbps NIC

## Slide 94: Network connection ToDo
Connection to Summit core (E-LAN, V-LAN)
  To send up-the-ramp smoothly, we may need more than 1Gbps. Need LACP configuration.
    PFS side for up-the-ramp to Gen2 is one g2cam host (TBC), need some care on LACP balancing.
  V-LAN is also through Summit core, could connect through trunk port configuration on Summit core and PFS core.
    Even if we select this, I want to keep separate connection for V-LAN and PFS-LAN to the host (in PFS network).
Connection between PFS core and SpS (ICS #579)
  There is a way to go on configuration to pass 4x300-400Mbps stream, but need to be cared in configuration both BEE and iSCSI storage.

## Slide 95: Host cluster at CB2F
Most of services are planned to run on VMs, such as MHS, logger, support infrastructure. Also PFI related actors are in consideration.
Some services (esp. DB) is planned as bare system, but could be on VM if performance is verified.
Host configuration (still in development):
iSCSI storage (108TB RAID6 w/2sp, 2x2U) x1
Dell R710 Xeon E5506 (2xAC, 2U) x2
Dell R410 Xeon E5640 (1xAC, 1U) x3
Dell R310 Xeon E3-? (1xAC +1 vacant, 1U) x1 (for DB?)

## Slide 96: Host cluster ToDo
Verify iSCSI storage performance with more realistic configuration
  Currently only write from 4xH4RG simulator – NFS server – iSCSI storage.
  Better to verify with running VMs, DB connections, with some data read/write (incl. sending up-the-ramp to Gen2)
IR data handling
  Original plan was host control computer at CB2F with large memory, which will do all for data management
    Read directly from SAM over 1Gbps network
    Save up-the-ramp FITS (single 2D HDU) to storage, and on memory
    Build final FITS file from data on memory (no read stream from storage for this)
  Currently, BEE reads data from SAM via USB, and saves to storage
    Something other need to care of building final FITS file etc.
Verify VM operation performance
  Mostly tested using PFS server cluster at IPMU for pfs.ipmu.jp
Integration of PFI control into VM cluster
  Need to check PCI passthrough performance and capability for PCIe extender.
    Or USB mount could work?
  Check network bandwidth requirement (for shared interface)
Host maintenance operation
  Health check with iDRAC etc.

## Slide 97: Status gathering
Most all of PFS ICS control modules (called as “actor”) are connected to the MHS, Messaging Hub Service/Server, and communicates to other modules only through the MHS. Status of each module are pushed from each actor itself, using normal message exchange way or its subset dedicated to status, and distributed to other modules by the MHS.
Status archive service is connected to the MHS as one actor, gathers all updates from every actors, and saves to a system database.
Gen2
MHS
g2t
g2cam
BCU1
RCU1
NCU1
BCU2 …
RCU2 …
NCU2 …
FPS
IIC
MPS
AGC
MAC
MLP1
SAS
STS

## Slide 98: Status viewer
PFS status viewer will be mainly used at the summit during night operation, but will also be used for engineering operation and monitoring, remote observation monitoring (e.g. Mitaka remote), or helping trouble shooting from remote. Therefore, at least multiple instance should be possible, and it is better to support wide variety of remote hosts even like mobile devices.
Using recent web technology, interactive GUI is quite easy to build as multi-platform including mobile devices using the same code. Also to access over network domain (or from different network domain, in other word), such method is more flexible than GUI window sharing. Although we might not use, it is easy to build 3D interactive status viewer using elements directly converted from 3D CAD file, and also we can provide URI based (or using fragment) snapshot to share status for later use.
Status archiver
MHS
jsonp provider
SHM or in same process
Web server
Browser
database
DB to json
SQL
Static HTML
jsonp or CORS

## Slide 99: Observation flow and its sequence
Basic concepts are
SPT+ETS coordinates exposure sequence and configuration well before observation (or run)
  SPT+ETS outputs a list of exposure configurations
    Set of targets with stars for field acquisition, focus check and auto guide
  Details in a following presentation by Kiyoto
Queue dispatcher in Gen2 picks next exposure configuration
  Or, by survey sequencer (or survey operator at summit)
  Once exposure finished and FITS generated, FITSs are transferred to on-site DRP at Hilo for QA processing
    QA results will be presented to operator at Summit for feedback
Gen2 commands next exposure configuration to IIC, and IIC handles instrument sequence
  Telescope pointing at the end of exposure (esp. InR angle) will be calculated in Gen2 and passed to IIC
    For FoV rotation by mod 60 degree (details in PFS-SE-IPMU-00007)
  (assuming) IIC to be main sequencer in between two exposures
    Except for moving to distant field (= slewing telescope largely)?
    Using Gen2 status and command as callback procedure

## Slide 100: Entire night operation sequence
Conditions and considerations for entire night operation sequence are:
Night operation starts from evening with checking instrument status. Some telescope related check will be performed by DayCrew2 called as “pre-check” for weekdays, and some instrument status will be checked during “pre-check” for PFS which directly relates to the telescope. Also health check of POpt2/PFI and Cs after each exchange will be required during instrument exchange work (refer other document/note on instrument exchange procedures).
  Sequence need include pre-check function – e.g. capable to operate AG camera
  Operational sequence for instrument exchange will be defined separated to this
  Sequence need include instrument health check before starting night operation
PFS plans to get calibration frames for all configurations executed at night, both flat (halogen lamp) and arc (three composited lamps). Since telescope need to point zenith to take these calibration frames using flat screen, also entire number of configurations will be around 50 (15min exposure for 10-14 hours) with 2-3min each required to complete, this operation is assumed to be performed after night operation – before starting daytime work keeping dome well dark.
Measuring and moving telescope focus position is normally performed two or three times per night (before observation, midnight and after observation), using object size scanning z direction of M2 or POpt(2). How PFS will do on this is unclear, but also PFS will check PF focus during exposure using focusing AG camera. If PFS need to take this kind of scanning data using AG camera, special mode need to be implemented.
Next slide shows flow diagram of “set of operations”, most of which will run in serial – like “pre-check” or “get calibration frames”.

## Slide 101: Entire night operation – diagram
End of daytime operation / work
“pre-check”
Health check on PFS subsystems
Start of night operation
End of night operation
Telescope focus (initial) check
Go to next field
Execute exposure
Take calibration frames
“Instrument health check prior to observations”
“Exposure operation”
“Calibration frames”
(TBD)

## Slide 102: Exposure operation
Concepts:
Coordination of procedure between two exposures as shorter as possible is a key to make observation more efficient.
  Run instrument configuration sequence in parallel as possible, especially for items takes long time.
Instrument integration and test over entire PFS will only be on telescope, verify as much as possible in each stage.
  Coordinate exposure configuration sequence into subsequences with simple interlocks.
  Plan to verify subsequences on subsystem AIT.

## Slide 103
PFS Basic Operation Sequence for Single Exposure as of 2016/08
Shutter Close
Exposure end
Exposure start
Shutter open
AutoGuide
Tel Slew
Az
EL
InR
ADC
Hexapod
SpS/BIA
Turn on
Turn off
(BIA ON)
IR up-ramp
IR data compose / transfer
CCD readout
CCD data transfer
IR up-ramp
IR detector reset
CCD wipe
On-site DRP processing
On-site DRP processing / Target selection by ETS
PFI/FFI
Turn on
Turn off
(PFI Fixed fiducial ON)
Field Acquisition
AutoGuide
FPS / MCS configuration
MCS final data
MPS
FPS
MCS
Move
Move
Move
Move
Continuous measurement
Exec sequence
A
B
C
D
E
F
AG Acquisition
E
Move home
Move
background?
Check at home
interlock

## Slide 104: System verification and integration
If design follows concepts well, PFS ICS software verification and integration flow will be hierarchic, continue validation at each level and to go next level of integration. Thanks to loosely coupled module based design using MHS, validation of each actor or combination of actors within one (sub-)sequence could be done without any other software module.
These subsystem or module(s) verification are written as sequences and developed as special actor – spsait or pfiait. Using them, software integration and test flow will be 1) per module (actor), 2) per subsystem, whose hardware are at one place before shipping to Subaru (A-E in a last slide), 3) full operational sequence at Subaru.
BCU
RCU
FPS
AGC
Subaru
NCU
ENU
xxxait
MPS
pre-ship verification on API of each actor
SpS/SM
PFI
pre-ship verification on subsequence and AIT sequence
g2t
MAC
PFS
operation
Verification of connection between PFS module and Subaru during pre-integration connectability test

## Slide 105: System verification and integration (at Subaru)
Last slide was mainly for software modules to control hardware, PFS also need to verify non-hardware control subsystems. This activity need to be done at Subaru using simulator and/or real controller, before point of delivery of hardware to Subaru, such as:
  g2t (to Gen2)
    PFS shares g2t with CHARIS, so basic function will be validated by CHARIS commissioning
    Some new functions need to be validated before or during PFS commissioning
      Push AG image (before start of commissioning), InR feed back (during first stage of PFI)
    Sequencing between IIC and Gen2 need to be tested also
      Callback for InR rotation, focusing, field acquisition, etc.
  MAC (to MLP1, V-LAN, etc.)
    Off-site communication test will be validated at melco factory
    Error signal conversion need to be tested during first stage of full commissioning
  SAS (Status)
    Can be tested well before commissioning (using dummy status generation)
  GUI for operator
    Plan not defined yet, but assuming Web interface, server side will be validated before commissioning, client side will be updated to the last stage of commissioning